Solaronics, Inc., Gas Fired Infrared Radiant Heaters Customizable Master Word Specifications. These specifications are provided to assist in specifying Solaronics, Inc. products.  A qualified design professional should review and edit the specifications to satisfy project requirements. For more information, contact: Solaronics, Inc., 3720 Lapeer Road, Auburn Hills, Michigan MI 48326; phone: 248-651-5333, fax: 248-651-0357, website: www.solaronicsusa.com, email: sales@solaronicsusa.com.

SECTION 23 55 23 - GAS-FIRED RADIANT HEATERS (FORMERLY SECTION 15542)

PART 1 - GENERAL

1.1	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions, and Division 01 Specification Sections apply to this Section.

1.2	SUMMARY

A.	Section includes:

1.	[Gas-Fired Infrared Radiant Tube Heaters.]

2.	[Gas-Fired High-Intensity Infrared Heaters.]

B.	Related Sections:

1.	Division 23, Section 23 10 00 "Facility Fuel Systems".

2.	Division 23, Section 23 51 00 "Breechings, Chimneys, and Stacks".

3.	Division 26, Section 26 05 00 "Common Work Results for Electrical".

1.3	REFERENCES

A.	Applicable Standards:

1.	American National Standards Institute (ANSI):

a.	Z83.19 - Gas-Fired High-Intensity Infrared Heaters.

b.	Z83.20 - Gas-Fired Low-Intensity Infrared Heaters.

2.	National Fire Protection Association (NFPA):

a.	54 - National Fuel Gas Code.

b.	70 - National Electric Code.

3.	Underwriters Laboratories Inc. (UL):

a.	486A - Wire Connectors and Soldering Lugs for Use with Copper Conductors.

b.	486B - Wire Connectors for Use with Aluminum Conductors.

1.4	SUBMITTALS

A.	Product Data: Include rated capacities, operating characteristics, physical dimensions, weights, furnished specialties, and accessories.

B.	Shop Drawings: Include field wiring diagrams of power, signal, and control wiring.

C.	Coordination Drawings: Include anchorages and attachments to structure and to supported equipment based on input from equipment installers.

D.	Field Quality-Control Test Reports: From Contractor.

E.	Operation and Maintenance Data: For gas-fired radiant heaters include installation, operation and maintenance manuals.

F.	Warranties: Special warranties specified in this Section.

1.5	QUALITY ASSURANCE

A.	Building Codes and Standards.

1.	[Gas-Fired High-Intensity Infrared Heaters shall be Design Certified by CSA to ANSI Z83.19. The supplier shall provide the CSA Certification Number and the heaters shall bear the CSA Seal of Certification.]

2.	Heaters shall comply with current Occupational Safety and Health (OSHA) Requirements.

3.	Heaters shall be furnished and installed in accordance with NFPA 54, local codes, building drawings and manufacturer's recommendations.

4.	Natural or mechanical means shall be provided to supply and exhaust at least 4 CFM per 1000 Btu/hour input of installed heaters.

5.	In locations used for the storage of combustible materials, signs shall be posted to specify the maximum permissible stacking height to maintain required clearances from the heater to the combustibles.

B.	Source Limitations: Obtain gas-fired radiant heaters through one source from a single manufacturer.

C.	Product Options: Drawings indicate size, profiles, and dimensional requirements of gas-fired radiant heaters and are based on the specific system indicated. Refer to Division 1, Section "Product Requirements."

D.	Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.6	WARRANTY

A.	Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of gas-fired radiant heater that fails in materials or workmanship within specified warranty period.

B.	Warranty Period:

1.	Gas-Fired High-Intensity Infrared Heaters:

- One (1) year on the entire heater, including burner and controls.

- Available limited lifetime warranty available on ceramic burner

PART 2 - PRODUCTS

2.1	MANUFACTURERS

A.	In other Part 2 articles where subparagraph titles below introduce lists, the following requirements apply for product selection:

1.	Manufacturers: Subject to compliance with requirements, provide products by the manufacturers specified.

2.2	GAS-FIRED HIGH INTENSITY INFRARED HEATERS  (SECTION 235523.16)

A.	Manufacturers:

1.	Solaronics, Inc. - Basis of design specification.

a.	Heaters shall be SOLARONICS:

i.	[STK-SERIES (2-stage)] or

ii.	[K-SERIES (single-stage)]

b.	Gas-Fired High-Intensity Infrared Heaters of series model numbers and inputs in MBTUH;

c.	Manufactured by: Solaronics, Inc., Rochester, Michigan 48307;

d.	Over 50 years of experience manufacturing gas-fired high-intensity infrared heaters, or comparable product by the following:

2.	Or equal.

B.	Description: Heater factory assembled, piped, wired, fully tested and ready to install and complying with ANSI Z83.19.

1.	[2-Stage Control: STK-SERIES (2-stage) heaters shall provide 2-stage control of Both Gas and Air to provide the most efficient and complete combustion at both high and low fire rates.]

a.	[Performance: 2-stage heaters shall stop energy overshoot, improve comfort and cut energy consumption when less heat is needed, yet provide more heat quickly when temperature falls sharply.]

- CSA Approval: Heater Design Certified by and bearing the label of CSA (formerly AGA, the American Gas Association).

- For commercial / industrial use only.

- For indoor installation only.

5.	Type of Gas: Heater designed and built to burn fuel gas with characteristics same as those of gas available at project site.

a.	[Natural Gas: Heaters designed to operate without adjustments when burning natural gas having a heat value of 1000 BTU per cubic foot with a specific gravity of .65.]

b.	[Propane Gas: Heaters designed to operate without adjustments when burning propane gas having a heat value of 2500 BTU per cubic foot with a specific gravity of 1.53.]

6.	Supply Inlet Gas Pressure:

a.	[Natural Gas: Heaters designed to satisfactorily operate on natural gas at a minimum supply inlet gas pressure of 7 inches water column (W.C.) and at a maximum supply inlet gas pressure of 14 inches W.C.]

b.	[Propane Gas: Heaters designed to satisfactorily operate on propane gas at a minimum supply inlet gas pressure of 11 inches water column (W.C.) and at a maximum supply inlet gas pressure of 14 inches W.C.]

7.	Design Features:

- Heaters capable of angle mounting from 5 to 30 degrees, without the use of an additional reflector.

b.	Heater of modular design employing multiple burners to achieve the specified input.

C.	Burner:

1.	Construction: Burner consists of ceramic combustion surface (emitter), aluminized-steel plenum chamber with stainless-steel surface retainers, aluminized-steel venturi tube, and aluminized-steel burner mounting bracket.

a.	Plenum chamber of 20 ga. (.035") corrosion-free aluminized steel, one-piece fabrication and seamless no-weld construction.

b.	Stainless-steel surface retainer of one-piece to hold the ceramic surface in place around its entire perimeter.

c.	Burner mounting bracket of 14 ga. (.083") aluminized steel for holding the burner assembly in place to achieve proper alignment of the surface, venturi and orifice.

2.	Removability: Burners removable with a single screw for cleaning or replacement without disconnecting any gas, electrical or hanging device.

D.	Emitter:

1.	Description: Ceramic combustion surface.

2.	Performance: Emitter comply with ANSI Z83.19, Section 2.10 Radiant Coefficient, without the use of a secondary re-radiating surface of either rods or screen.

3.	Capability: Emitter capable of reaching temperatures up to 1850 degrees F (an incandescent appearance) and withstand thermal shock when water quenched.

4.	Design Features: Emitter of cordierite-based grooved ceramic with alternate rows of 230 perforations per square inch terminate at the bottom of slots making half the flame below the top ceramic surface creating more contact between flame and surface.  This design increases ceramic surface temperature and radiant output with lower gas input and greater resistance to drafts.

5.	Installed Position: Emitter horizontal when heater installed at 0 degrees.

E.	Main Frame:

1.	Construction: Heater frame of 16 ga. (.065") corrosion-free aluminized steel and of no-weld construction.

2.	Design Features: Heater frame shall have double turned upper edge and two (2) corner reinforcement brackets for rigidity.

3.	Mounting Points: The side frames shall have four (4) 3/8" diameter holes for easy mounting with S-hooks and chain.

F.	Reflector:

1.	Material: Reflectors of 21 ga. (.032") highly polished aluminum.

2.	Reflectivity: Reflectors reflectivity of not less than 98%.

3.	Design Features: Reflector of standard design (shape), with .352 square feet of reflective area per linear foot, double turned edge for rigidity and mounted to heater at factory.

G.	Heater Controls: Control designation based on: gas type, number of stages, voltage, and ignition type.

1.	[STN: natural gas, 2-stage, 24 VAC direct spark ignition control, 100% safety shut off with flame monitoring, and 12 VA maximum power consumption.]

a.	[Control capable of 2-stage operation on low and high modes in conjunction with a 2-stage microprocessor thermostat.]

2.	[STL: propane gas, 2-stage, 24 VAC direct spark ignition control, 100% safety shut off with flame monitoring, and 12 VA maximum power consumption.]

a.	[Control capable of 2-stage operation on low and high modes in conjunction with a 2-stage microprocessor thermostat.]

3.	[QSAN: natural gas, single-stage, 24 VAC direct spark ignition control, 100% safety shut off with flame monitoring, and 6 VA maximum power consumption.]

4.	[QSAL: propane gas, single-stage, 24 VAC direct spark ignition control, 100% safety shut off with flame monitoring, and 6 VA maximum power consumption.]

5.	[DSAN: natural gas, single-stage, 115 VAC direct spark ignition control, 100% safety shut off with flame monitoring, and 6 VA maximum power consumption.]

6.	[DSAL: propane gas, single-stage, 115 VAC direct spark ignition control, 100% safety shut off with flame monitoring, and 6 VA maximum power consumption.]

7.	[TAN: natural gas, single-stage, millivolt manual pilot ignition control, 100% safety shut off of constant pilot and main burner(s) in case of pilot outage.]

a.	[Gas regulator field adjustable.]

b.	[Pilot flame concealed to protect it from drafts.]

c.	[Control supplied with 35' of 18-2 wire and a millivolt thermostat.]

d.	[Control operates with no external electrical power, but instead uses milli-voltage generated by pilot flame.]

8.	[TAL: propane gas, single-stage, millivolt manual pilot ignition control, 100% safety shut off of constant pilot and main burner(s) in case of pilot outage.]

a.	[Gas regulator field adjustable.]

b.	[Pilot flame concealed to protect it from drafts.]

c.	[Control supplied with 35' of 18-2 wire and a millivolt thermostat.]

d.	[Control operates with no external electrical power, but instead uses milli-voltage generated by pilot flame.]

H.	Capacities and Characteristics:

1.	Gas Input:

- [Specify MBTUH = 1000 Btu/hr.]

- [2-stage models: natural gas 100/50, 150/100 and 200/100 MBTUH; propane gas 90/45, 120/80 and 160/80 MBTUH.]

- [Single-stage models: natural gas 30, 35, 40, 45, 50, 55, 60, 70, 75, 80, 85, 90, 95, 100, 110, 120, 125, 130, 135, 150, 160, 175 and 200 MBTUH; propane gas 50, 70, 75, 80, 85, 90, 120 and 160 MBTUH.]

2.	Gas Supply Piping Connection: 1/2 inch FPT.

3.	Altitude:

a.	[Sea level to 2000 feet.]

b.	[Above 2000 feet.]

I.	Accessories: Certified by CSA for use with heater.

1.	Heat-Deflector Shield for heaters of 30 thru 100 MBTUH to reduce required clearance to combustible materials above heater.

2.	Secondary Re-radiating Wire Grid to improve heater performance in drafty areas and increase efficiency.

3.	Parabolic Reflector Extension to concentrate radiant infrared energy for high mounting height applications or for spot heating.

4.	Protective Screen for locations where foreign objects may damage the heater's ceramic surface.

5.	Stainless-steel flexible connector with manual valve.

6.	Hanger chain with S-hooks.

7.	Pre-assembled chain mounting kit.

2.4	TEMPERATURE CONTROL

A.	Wires and Cables: Specified in Division 23, Section "Control/Signal Transmission Media."

B.	Sensor, Components, and Wiring: Specified in Division 23, Section "HVAC Instrumentation and Controls."

C.	[Thermostat: 2-stage, 24-VAC wall-mounting type with 50 to 90 degree F operating range.]

D.	[Thermostat: Single-stage, 24-VAC wall-mounting type with 50 to 90 degree F operating range.]

E.	[Thermostat: Single-stage, 115-VAC wall-mounting type with 50 to 90 degree F operating range.]

F.	[Locking Thermostat Guard.]

G.	[Control Transformer: 120 to 24-VAC.]

PART 3 - EXECUTION

3.1	EXAMINATION

A.	Examine roughing-in for radiant heater piping systems to verify actual locations of piping connections before equipment installation.

B.	Proceed with installation only after unsatisfactory conditions have been corrected.

3.2	INSTALLATION

A.	Install radiant heaters in accordance Manufacturer's requirements in the Installation, Operation, and Maintenance Manual supplied with each heater.

B.	Install radiant heaters level and plumb.

C.	Install and connect gas-fired radiant heaters and associated fuel and vent features and systems according to NFPA 54, applicable local codes and regulations, and manufacturer's written installation instructions.

D.	Suspend Units: Suspend from substrate using chain hanger kits and building attachments.

E.	Maintain manufacturer's required clearance to combustibles.

3.3	CONNECTIONS

A.	Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B.	Install piping adjacent to heater to allow service and maintenance.

C.	Gas Piping: Comply with applicable requirements in Division 23, Section "Facility Fuel Gas Piping."  Connect gas piping to heater gas inlet; provide union with enough clearance for burner removal and service.  Provide CSA-approved flexible gas connector.

D.	Connect vents according to Division 23, Section "Breechings, Chimneys, and Stacks."

E.	Electrical: Comply with applicable requirements in Division 26 Sections.

1.	Install electrical devices furnished with heaters but not specified to be factory mounted.

2.	Install control and power wiring and conduit for controller, sensors, [mechanical ventilation relays and interlock switches,] and heaters.

F.	Ground equipment according to Division 26, Section "Grounding and Bonding for Electrical Systems."

G.	Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.4	FIELD QUALITY CONTROL

A.	Manufacturer's Field Service: Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including piping and electrical connections.

1.	Verify proper electrical earth grounding.

2.	Verify electrical supply polarity is correct.

3.	Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

4.	Test Reports: Prepare a written report to record the following:

a.	Test procedures used.

b.	Test results that comply with requirements.

c.	Test results that do not comply with requirements and corrective action to achieve compliance with requirements.

3.5	COMMISSIONING

A.	Review Manufacturer's instructions before commissioning or making any adjustments to the heater.

B.	Verify that gas-fired radiant heaters are installed and connected according to Manufacturer's instructions.

C.	Measure gas supply inlet pressure and adjust as necessary at startup per Manufacturer's instructions.

D.	Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3.6	ADJUSTING

A.	Adjust initial temperature [and humidity] set points.

B.	Adjust burner and other unit components following Manufacturer's instructions for optimum heating performance and efficiency.

3.7	DEMONSTRATION

A.	Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain gas-fired radiant heaters. Refer to Division 01.

END OF SECTION 23 55 23 (FORMERLY SECTION 15542)